Revised July 22, 2025

Section 230900 Control Valves

2-way Industrial Ball Valves (Belimo VSS Series)

- The control valve and actuator assembly shall be provided and delivered from a single manufacturer.

- Manufactured, brand labeled or distributed by Belimo.

- The manufacturer shall warrant all components for a period of 2 years from the date of production.

- Actuators for valves shall be cULus listed and be manufactured under ISO 9001 International Quality Control Standards.

- Where indicated, provide actuator to fail to an end position (open or closed).

- Actuators shall be protected from overload at all angles of rotation.

- Control valve and actuator assembly shall be capable of closing valve against 150% system pump shutoff head for water; 150% steam design pressure.  3-way mixing valves shall be capable of closing valve against 150% of system differential pressure.

- Control valve bodies shall be A351-CF8M 316 stainless steel with PEEK/PTFE or RTPFE bearings, MPTFE stem packing and PTFE body seal.  316 stainless steel ball and retainer.

- Media water temperature shall be -22oF to +298oF (-30oC to +148oC) with maximum 60% glycol solution   or 50 psig (344 kPa) steam.

- Valve shall be a modified equal percentage flow characteristic with ANSI Class VI Leakage.