Revised July 22, 2025

Section 230900 Control Valves

Characterized Control Valves (Belimo CCV)

- The control valve and actuator assembly shall be provided and delivered from a single manufacturer.

- Manufactured, brand labeled or distributed by Belimo.

- The manufacturer shall warrant all components for a period of 5 years from the date of production.

- Actuators for valves shall be cULus listed and be manufactured under ISO 9001 International Quality Control Standards.

- Where indicated, provide actuator to fail to a predetermined position.

- Actuators shall be provided with a means of manual override upon power loss.

- Actuators shall be protected from overload at all angles of rotation.

- Control valve and actuator assembly shall be capable of closing valve against 150% system pump shutoff head for water.  3-way mixing valves shall be capable of closing valve against 150% of system differential pressure.

- Control valve bodies shall be nickel plated (forged) brass or cast iron GG25.  Stainless steel ball and blow-out proof stem with PTFE and double EPDM O-Rings.  Valve body shall incorporate a TefzelTM, Ryton PPS or stainless steel characterizing disc.

Note to Specifier:  Option for chrome plated ball and stem can be substituted for ½” and ¾” sizes only.

- Media water temperature shall be 0oF to 250oF (-18oC to +120oC) with maximum 60% glycol solution.

- Valve (A-AB) shall be equal percentage flow characteristic with 0% Leakage