Revised July 22, 2025

Section 230900 Control Valves

High Temperature Characterized Ball Valves (Belimo HTCCV)

- The control valve and actuator assembly shall be provided and delivered from a single manufacturer.

- Manufactured, brand labeled or distributed by Belimo.

- The manufacturer shall warrant all components for a period of 5 years from the date of production.

- Actuators for valves shall be cULus listed and be manufactured under ISO 9001 International Quality Control Standards.

- Where indicated, provide actuator to fail to a predetermined position.

- Actuators shall be protected from overload at all angles of rotation.

- Control valve and actuator assembly shall be capable of closing valve against 150% system pump shutoff head for water; 150% steam design pressure.  3-way mixing valves shall be capable of closing valve against 150% of system differential pressure.

- Control valve bodies shall be DZR brass.  Stainless steel ball and blow-out proof stem with TFE and FKM O-ring and double EPDM O-Rings.  Valve body shall incorporate ETFE (TefzelTM).

- Media water temperature shall be 60oF to 266oF (-16oC to +130oC) with maximum 60% glycol solution or 15 psig (103kPa) maximum steam inlet at 250oF (120oC).

- Valve (A-AB) shall be equal percentage flow characteristic with 0% Leakage