Revised July 22, 2025

Section 230900 Control Valves

V Ball Valves (Belimo V Ball)

- Manufactured, brand labeled or distributed by Belimo.

- The manufacturer shall warrant all components for a period of 2 years from the date of production.

- Actuators for valves shall be cULus listed and be manufactured under ISO 9001 International Quality Control Standards.

- Where indicated, provide actuator to fail to a predetermined position.

- Actuators shall be provided with a means of manual override upon power loss.

- Actuators shall be protected from overload at all angles of rotation.

- Control valve and actuator assembly shall be capable of closing valve against 150% system pump shutoff head for water; 150% steam design pressure.  3-way mixing valves shall be capable of closing valve against 150% of system differential pressure.

- Control valve bodies shall be carbon steel.  Stainless steel ball and stem with Teflon seat and ALFAS O-Rings.  Valve body shall incorporate hardened chrome plated stainless steel characterizing ball.

- Media water temperature shall be -22 to +380oF (-30 to +193oC) with maximum 60% glycol solution.  Maximum steam inlet pressure of 150 psi (1034 kPa).

- Valve shall be equal percentage flow characteristic with ANSI Class IV Leakage