Revised July 22, 2025

Section 230900 Control Valves

Zone Valves (Belimo ZoneTight)

- The control valve and actuator assembly shall be provided and delivered from a single manufacturer.

- Manufactured, brand labeled or distributed by Belimo.

- The manufacturer shall warrant all components for a period of 5 years from the date of production.

- Actuators for valves shall be cULus listed and be manufactured under ISO 9001 International Quality Control Standards.

- Where indicated, provide actuator to fail to a predetermined position.

- Valve assembly shall be provided with a means of manual override upon power loss.

- Actuators shall be protected from overload at all angles of rotation.

- Actuator adaptation shall permit calibration of the analog input control signal to the control valve opening.

- Control valve and actuator assembly shall be capable of closing valve against 150% system pump shutoff head for water.  3-way mixing valves shall be capable of closing valve against 150% of system differential pressure.

- Control valve bodies shall be forged brass.  Chrome plated brass ball and blow-out proof stem with PTFE and double EPDM O-Rings.

- Media water temperature shall be 0oF to 212oF (-18oC to +1oC) with maximum 60% glycol solution.

- 2-way valve (A-AB) shall be equal percentage flow characteristic with 0% Leakage.  3-way diverting shall be a linear flow characteristic.

- Maximum flow coefficient (Cv) shall be field adjustable without the use of specialized tools.